RDCJ-DY Series Impulse Voltage Generator

RDCJ-DY series impulse voltage generator is used for impulse voltage test of lightning impulse voltage full wave , lightning impulse voltage chopped wave and operation impulse voltage wave which apply to electrical equipment ect. Multiple waveform impulse voltage generator can produce eight kinds of waveforms of standard lightning wave, operation wave, lightning chopped wave, oscillating lightning wave, oscillating operation wave, line insulator steep wave, composite insulator steep wave, transformer induction operation wave. The technology index accords with national standard and IEC standard, is in the leading position at home and has reached an advanced level in the world

- Product Features

1. Complete sets, full voltage classes.
2. Small loop inductance, take the band elimination filter measures, still produce standard impulse wave in the large-capacity load, large load capacity, high voltage utilization, convenient to adjust wave.

3. Simple operation, excellent synchronization performance, reliable action.
4. Constant current charging technology, high automation, strong anti-interference performance.
5. Digital measurement and analysis system and computer on line processing system for impulse test data, greatly improve the test technology and efficiency.

- Product Specifications and Technical Parameters

| Standard Voltage | Impulse Capacitance(µF) |  | Classes Capacitance(µF) |  | Impulse Energy(kJ) | Classes Voltage(kV) | Class |  | Weight(kg) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ±300~±900 | 0.133~0.111 |  | 0.4~1 |  | 6~45 | ±100 | 3~9 |  | 547~1378 |
| ±1000~±1600 | 0.05~0.0937 |  | 0.5~1.5 |  | 25~120 |  | 10~16 |  | 1366~1880 |
| ±1800~±2400 | 0.056~0.0833 |  | 0.5~1 |  | 90~240 | ±200 | 9~12 |  | 7353~11574 |
| ±2800~±3200 | 0.0357~0.0625 |  | 0.5~1.5 |  | 140~320 |  | 14~16 |  | 10266~15680 |
| ±3600~±4800 | 0.0278~0.03125 |  | 0.5~2 |  | 80~240 |  | 18~24 |  | 15480~23500 |
| Technique Parameters |  |  |  |  |  |  |  |  |  |
| Items |  |  |  | 1,1.2/50µs 2,250/2500µs 3,2~5µs etc waveforms |  |  |  |  |  |
| Output Peak Value |  |  |  | 100~10000kV |  |  |  |  |  |
| T1 Wave Front Time |  |  |  | 1.2µs±30% |  |  |  |  |  |
| T2 Wave Tail Time |  |  |  | 50µs±20% |  |  |  |  |  |
| Reverse Overshoot |  |  |  | <20% |  |  |  |  |  |
| Voltage Polarity |  |  |  | Positive/negative(manual shifting) |  |  |  |  |  |
| Waveform Shift |  |  |  | Auto shifting |  |  |  |  |  |
| Charging Time |  |  |  | 10s~999s, set arbitrarily |  |  |  |  |  |
| Instability of charging voltage |  |  |  | <1% |  |  |  |  |  |
| External Input |  |  |  | 50Hz/60Hz |  |  |  |  |  |
| Trigger Method |  |  |  | Auto or manual, can single trigger |  |  |  |  |  |
| Trigger Maloperation rate |  |  |  | <1% |  |  |  |  |  |
| Trigger Range |  |  |  | 100% rated charging voltage |  |  |  |  |  |
| Display Screen |  |  |  | 17-inch TFT color screen |  |  |  |  |  |
| Measurement Display Precision |  |  |  | Better than 3% |  |  |  |  |  |
| Tested Product Residual Voltage |  |  |  | <5kV |  |  |  |  |  |
| Voltage Measurement |  |  |  | Use damped impulse divider |  |  |  |  |  |
| Oscilloscope |  |  |  | TBS series, optional |  |  |  |  |  |
| Insulation Strength |  |  |  | ≤500V RMS (common to ground refer PE) |  |  |  |  |  |
| General Parameters |  |  |  |  |  |  |  |  |  |
| Power Source |  |  |  | AC220V±10%, 50/60Hz |  |  |  |  |  |
| Environment Temperature |  |  |  | -10±40ºC |  |  |  |  |  |
| Relative Humidity |  |  |  | 35%-85% RH (no condensation) |  |  |  |  |  |
| Ground Resistance |  |  |  | ≤0.5Ω |  |  |  |  |  |
| Structure Type |  |  |  | Open structure, independent control cabinet and main body, optical fiber connection |  |  |  |  |  |
| Control Console |  |  |  | 1.8M(length)*1.2M(height)*1M(width) |  |  |  |  |  |
| No conductive dust, no fire and explosion hazards, no corrosive metal and insulation gas, waveform |  |  |  |  |  |  |  |  |  |
| of power voltage is sine wave, distortion <5%. |  |  |  |  |  |  |  |  |  |
| Equipment model selection parameters |  |  |  |  |  |  |  |  |  |
| Nominal Total Voltage kV |  | Class | Impulse Capacitance (μF) |  | Impulse Level Capacitance(μF) | Total Charging Power(kJ) |  | Application |  |
| ±300~±900 |  | 3~9 | 0.133~0.111 |  | 0.4~1 | 6~45 |  | 35~110kV |  |
| ±1000~±1600 |  | 10~16 | 0.05~0.0937 |  | 0.5~1.5 | 25~120 |  | <220kV |  |
| ±1800~±2400 |  | 9~12 | 0.056~0.0833 |  | 0.5~1 | 90~240 |  | 220kV~500kV |  |
| ±2800~±3200 |  | 14~16 | 0.0357~0.0625 |  | 0.5~1.5 | 140~320 |  |  |  |
| ±3600~±4800 |  | 18~24 | 0.0278~0.03125 |  | 0.5~2 | 80~240 |  |  |  |
| Minimum time difference between pulse |  |  | 30s |  |  | 40s |  |  |  |
| Generator capacity per level |  |  | ≤1600kV use 100kV single side charging 1 |  |  | ≥1600kV use 100kV double sides charging |  |  |  |