| MODEL | 31 10KS PLUS | 31 15KS PLUS | 31 20KS PLUS |
| --- | --- | --- | --- |
| Rated power | 10KVA/8KW | 15KVA/12KW | 20KVA/16KW |
| Input | Range of voltage(full load) | 207~475Vac 3P4W+G |
|  | Range of frequency | 40-70Hz(adjusted) |
|  | Power factor | ≥0.95 |
| output | Rated voltage | 220Vac(1±1%) 1P2W+G |
|  | Frequency | 1.The output frequency synchronizes with the input frequency when the input frequency is in the range of 46 Hz~ 54 Hz. 2.The output frequency is 50Hz when the input frequency is not in the range of 40 Hz~ 46 Hz and 54Hz~60Hz. 3.BAT mode:50Hz. |
|  | Rated current | 45A | 68A | 91A |
|  | Power factor | 0.8 |
|  | Distortion | ≤3% |
|  | Ratio | 3:1 |
|  | Over load | 105% ±5% < Load ≤ 125% ± 5% 60s transfer to bypass 125% ±5% < Load < 135% ± 5% 30s transfer to bypass Load > 135% ± 5%, 300ms transfer to bypass |
| Line—bat transfer time | 0ms |
| Efficiency | > 92% |
| Battery | Rated voltage | 192Vdc |
|  | Number | 16 |
|  | Charging current | 5.5A |
| Size (L*W*H)mm | 533*260*501 |
| Weight | 23kg | 32kg | 33kg |
| Work temp.(℃) | 0℃~40℃ |
| Work humidity | 20%~95% |
| Noise(dB) | ≤60dB |

31 10-20K PLUS specs