Rack Mount -Tower 1-3Kva Specification

1. 1 Electrical

| Model | RMT1K | RMT1KL | RMT2K | RMT2KL | RMT3K | RMT3KL |
| --- | --- | --- | --- | --- | --- | --- |
| Rating | 1KVA/900W | 2KVA/1800W | 3KVA/2700W |
| Input | Input phase | Single phase & earth ground |
|  | Voltage range | (90±5)VAC~(290±5)VAC |
|  | Power factor | ≥0.99 |
|  | Voltage range of bypass | （80±5)VAC～（286±5)VAC （default：80VAC~264VAC Could be adjusted by software） |
| Output | Output phase | Single phase & earth ground |
|  | Rated voltage | 220VAC ① |
|  | Power factor | 0.9 |
|  | Voltage precision | ±2% |
|  | Output wave form(AC&battery modes) | Pure sine wave |
|  | Output frequency | Normal mode | 1. synchronize with the input frequency in the range 46 Hz～54 Hz 2. 50Hz (40Hz<input frequency <46Hz , 54Hz<input frequency <60Hz) 3.Can be set as 60Hz |
|  |  | Battery mode |  |
|  | Inverter overload capacity（Utility power，25℃） | 105%±5%<Load≤125%±5% 50s transfer to bypass 125%±5%< Load <150%±5% 25s transfer to bypass Load > 150%±5%,300ms transfer to bypass |
|  | Transfer time | 0ms （Normal mode←→ Battery mode） |
|  |  | <4ms（Normal mode←→Bypass mode） |
|  | Crest factor | 3:1 |
| Battery | Batteries voltage | 36VDC | 72VDC/96VDC | 96VDC |
|  | Battery Quantity | 3pcsx7AH | Long backup ext battery | Standard backup | Long backup ext battery | Standard backup | Long backup ext battery |
|  | Battery Type | Sealed lead acid maintenance free (SLMF) |
|  | Backup Time（25℃） | Full load≥5min (Standard) |
|  | Charging current | 1A | 6A | 1A | 5.5A | 1A | 5.5A |

- Note1: Output voltage can be set on LCD: 200V/208V/220V/230V/240V.

Specifications

- 2 Physical

| Model | WxDxH(mm) | Weight(kg) |
| --- | --- | --- |
| 1K | 482X450X88 (2U) | 13.7KG |
| 2K | 482X665X132 (3U) | 28KG |
| 3K | 482X665X132 (3U) | 32.5KG |
| 1KS | 482X450X88 (2U) | 7.2KG |
| 2KS | 482X450X88 (2U) | 9.7KG |
| 3KS | 482X450X88 (2U) | 9.7KG |

1. 3 Environmental

| Item | Normal range |
| --- | --- |
| Ambient temperature | 0℃～40℃ |
| Environment humidity | 20%～90%（No condensation） |
| Altitude | Lower than 1000m: no derating Over 1000m :1% derating for every 100m rise |
| Storage temperature | -15℃～45℃ |

1. 4 EMC

| Item | Standard | Level |
| --- | --- | --- |
| ESD | IEC61000-4-2 | LEVEL4 |
| RS | IEC61000-4-3 | LEVEL3 |
| EFT | IEC61000-4-4 | LEVEL4 |
| Surge | IEC61000-4-5 | LEVEL4 |

1.5 Safety

Comply with GB4943-2001, IEC62040-1 and CE requirements.

1.6 Industry Standard

Comply with EN62040，YD/T 1095-2000 requirements.

Model Picture:

RMT1-3Kva (19” x 2U) , LCD auto rotate